## Tabelle1
Condensing Unit
Refrigerant: |  | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a
Evaporating dew point temperature: | °C | -3.3 | -3.3 | -3.3 | -3.3 | -3.3 | 2 | -1.9 | -3.3 | -3.3 | -3.3
Evaporating pressure: | bar | 2.596 | 2.596 | 2.596 | 2.596 | 2.596 | 3.147 | 2.729 | 2.596 | 2.596 | 2.596
Useful superheat: | K | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.2 | 7.8 | 5.4 | 5.4 | 5.4
Additional superheat: | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Return gas temperature: | °C | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 7.2 | 5.8 | 2.1 | 2.1 | 2.1
Ambient temperature: | °C | 32 | 36 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
Subcooling: | K | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Additional subcooling: | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rating conditions: |  | Custom | Custom | Custom | Custom | Custom | Custom | Custom | Custom | Custom | Custom
Required cooling capacity: | kW | 3.072 | 2.523 | 3.617 | 2.332 | 3.349 | 0.833 | 1.977 | 2.811 | 1.88 | 3.13
Model |  | OP-MPXM046MLP00E | OP-MPXM034MLP00E | OP-MPXM046MLP00E | OP-MPGM033AJP00G | OP-MPXM046MLP00E | OP-MCGC015SCA00G | OP-MPGM033AJP00G | OP-MPXM034MLP00E | OP-MPGM033AJP00G | OP-MPXM046MLP00E
Code number |  | 114X4284 | 114X4264 | 114X4284 | 114X4220 | 114X4284 | 114X0448 | 114X4220 | 114X4264 | 114X4220 | 114X4284
Compressor model |  | MLZ021T4 | MLZ015T4 | MLZ021T4 | CAJ4511Y | MLZ021T4 | SC15GX | CAJ4511Y | MLZ015T4 | CAJ4511Y | MLZ021T4
Product range |  | Optyma™ Plus | Optyma™ Plus | Optyma™ Plus | Optyma™ Plus | Optyma™ Plus | Optyma™ | Optyma™ Plus | Optyma™ Plus | Optyma™ Plus | Optyma™ Plus
Product version |  | P00 | P00 | P00 | P00 | P00 | A00 | P00 | P00 | P00 | P00
Refrigerant |  | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a
Cooling [kW] |  | 3.967 | 2.819 | 3.967 | 2.332 | 3.967 | 1.053 | 2.469 | 2.95 | 2.332 | 3.967
COP cooling [W/W] |  | 2.94 | 2.57 | 2.94 | 2.43 | 2.94 | 1.75 | 2.51 | 2.89 | 2.43 | 2.94
Total power [kW] |  | 1.352 | 1.097 | 1.352 | 0.961 | 1.352 | 0.602 | 0.984 | 1.02 | 0.961 | 1.352
Total current [A] |  | 2.86 | 3.014 | 2.86 | 4.817 | 2.86 | 3.57 | 4.929 | 2.906 | 4.817 | 2.86
Frequency [Hz] |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Power supply |  | 380 - 400 V 3 ph | 380 - 400 V 3 ph | 380 - 400 V 3 ph | 220 - 240 V 1 ph | 380 - 400 V 3 ph | 220 - 240 V 1 ph | 220 - 240 V 1 ph | 380 - 400 V 3 ph | 220 - 240 V 1 ph | 380 - 400 V 3 ph
Tc [°C] |  | 40.7 | 43 | 40.7 | 39.1 | 40.7 | 50.2 | 39.4 | 39.1 | 39.1 | 40.7
Ecodesign
Model: OP-MPXM046MLP00E. Compliant with Ecodesign 2018
Refrigerant: R134a
Item | Unit | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value
Evaporating temperature | °C | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10
Parameters at full load and ambient temperature 32,0 °C
Rated cooling capacity | kW | 2.998 | 2.216 | 2.998 | 1.74 | 2.998 | 0.67 | 1.74 | 2.216 | 1.74 | 2.998
Rated power input | kW | 1.289 | 0.983 | 1.289 | 0.849 | 1.289 | 0.463 | 0.849 | 0.983 | 0.849 | 1.289
Rated COP |  | 2.33 | 2.25 | 2.33 | 2.05 | 2.33 | 1.45 | 2.05 | 2.25 | 2.05 | 2.33
Parameters at full load and ambient temperature 25,0 °C
Cooling capacity | kW | 3.217 | 2.378 | 3.217 | 1.922 | 3.217 | 0.727 | 1.922 | 2.378 | 1.922 | 3.217
Power input | kW | 1.136 | 0.865 | 1.136 | 0.811 | 1.136 | 0.446 | 0.811 | 0.865 | 0.811 | 1.136
COP |  | 2.83 | 2.75 | 2.83 | 2.37 | 2.83 | 1.63 | 2.37 | 2.75 | 2.37 | 2.83
Parameters at full load and ambient temperature 43,0 °C
Cooling capacity | kW | 2.634 | 1.958 | 2.634 | 1.44 | 2.634 | 0.563 | 1.44 | 1.958 | 1.44 | 2.634
Power input | kW | 1.565 | 1.205 | 1.565 | 0.897 | 1.565 | 0.492 | 0.897 | 1.205 | 0.897 | 1.565
COP |  | 1.68 | 1.62 | 1.68 | 1.6 | 1.68 | 1.14 | 1.6 | 1.62 | 1.6 | 1.68
Cold Room Controller
Power supply
Voltage |  | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz | 230 V~ ± 10% 50Hz / 60Hz
Power consumption (electronics only) |  | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA | ~ 7 VA
Cold room conditions
Operating temperature |  | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C | -5 to 50°C
Storage temperature |  | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C | -10 to 70°C
Relative humidity |  | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration. | Less than 90% - Not condensed. No shock influence/vibration.
General characteristics
Type of sensors |  | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210 | EKS 221, code no.: 084N3210
Resolution |  | 0.1 K | 0.1 K | 0.1 K | 0.1 K | 0.1 K | 0.1 K | 0.1 K | 0.1 K | 0.1 K | 0.1 K
Sensor read precision |  | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K | ± 0.5 K
Read range |  | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C | -45…+45 °C
Digital inputs
Requirements to contact |  | Gold plating | Gold plating | Gold plating | Gold plating | Gold plating | Gold plating | Gold plating | Gold plating | Gold plating | Gold plating
Output characteristics - max. applicable load (230 V AC)
Compressor |  | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3) | 1500W (AC3)
Defrost |  | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1) | 3000W (AC1)
Fans |  | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3) | 500W (AC3)
Room light |  | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1) | 800W (AC1)
Alarm contact (non-powered contact) |  | 100W | 100W | 100W | 100W | 100W | 100W | 100W | 100W | 100W | 100W
General electrical protection |  | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA
Dimensions
Dimensions |  | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL) | 168 mm x 97 mm x 262 mm (HxPxL)
Insulation / mechanical characteristics
Housing protection rating |  | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65 | IP65
Housing material |  | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS | Self-extinguishing ABS
Type of insulation |  | Class II | Class II | Class II | Class II | Class II | Class II | Class II | Class II | Class II | Class II
Ordering
Code number |  | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200 | 080Z3200
Liquid Line
Refrigerant: |  | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a
Mass flow in line: | kg/h | 96.69 | 70.39 | 96.69 | 55.94 | 96.69 | 27.8 | 58.28 | 70.8 | 55.94 | 96.69
Evaporating temperature: | °C | -3.3 | -3.3 | -3.3 | -3.3 | -3.3 | 2 | -1.9 | -3.3 | -3.3 | -3.3
Evaporating pressure: | bar | 2.596 | 2.596 | 2.596 | 2.596 | 2.596 | 3.147 | 2.729 | 2.596 | 2.596 | 2.596
Useful superheat: | K | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.2 | 7.8 | 5.4 | 5.4 | 5.4
Additional superheat: | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Discharge temperature: | °C | 60.5 | 63.3 | 60.5 | 58.5 | 60.5 | 69.3 | 60.8 | 58.6 | 58.5 | 60.5
Cooling capacity: | kW | 3.967 | 2.819 | 3.967 | 2.332 | 3.967 | 1.053 | 2.469 | 2.95 | 2.332 | 3.967
Heating capacity: | kW | 5.068 | 3.656 | 5.068 | 2.949 | 5.068 | 1.381 | 3.1 | 3.731 | 2.949 | 5.068
Condensing temperature: | °C | 40.7 | 43 | 40.7 | 39.1 | 40.7 | 50.2 | 39.4 | 39.1 | 39.1 | 40.7
Condensing pressure: | bar | 10.35 | 11.02 | 10.35 | 9.913 | 10.35 | 13.23 | 10.01 | 9.933 | 9.913 | 10.35
Subcooling: | K | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Additional subcooling: | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
System and line: |  | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line | Dry - Liquid line
Pressure drop | bar | 7.755 | 8.423 | 7.755 | 7.318 | 7.755 | 10.09 | 7.28 | 7.337 | 7.318 | 7.755
Saturation temperature drop | K | 44 | 46.3 | 44 | 42.4 | 44 | 48.2 | 41.4 | 42.4 | 42.4 | 44
Suction Line
Refrigerant: |  | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a | R134a
Mass flow in line: | kg/h | 96.69 | 70.39 | 96.69 | 55.94 | 96.69 | 27.8 | 58.28 | 70.8 | 55.94 | 96.69
Evaporating temperature: | °C | -3.3 | -3.3 | -3.3 | -3.3 | -3.3 | 2 | -1.9 | -3.3 | -3.3 | -3.3
Evaporating pressure: | bar | 2.596 | 2.596 | 2.596 | 2.596 | 2.596 | 3.147 | 2.729 | 2.596 | 2.596 | 2.596
Useful superheat: | K | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.2 | 7.8 | 5.4 | 5.4 | 5.4
Additional superheat: | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Discharge temperature: | °C | 60.5 | 63.3 | 60.5 | 58.5 | 60.5 | 69.3 | 60.8 | 58.6 | 58.5 | 60.5
Cooling capacity: | kW | 3.967 | 2.819 | 3.967 | 2.332 | 3.967 | 1.053 | 2.469 | 2.95 | 2.332 | 3.967
Heating capacity: | kW | 5.068 | 3.656 | 5.068 | 2.949 | 5.068 | 1.381 | 3.1 | 3.731 | 2.949 | 5.068
Condensing temperature: | °C | 40.7 | 43 | 40.7 | 39.1 | 40.7 | 50.2 | 39.4 | 39.1 | 39.1 | 40.7
Condensing pressure: | bar | 10.35 | 11.02 | 10.35 | 9.913 | 10.35 | 13.23 | 10.01 | 9.933 | 9.913 | 10.35
Subcooling: | K | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Additional subcooling: | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
System and line: |  | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line | Dry - Suction line
Pressure drop | bar | 0.002 | 0.001 | 0.002 | 0.003 | 0.002 | 0.002 | 0.003 | 0.001 | 0.003 | 0.002
Saturation temperature drop | K | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cold Room Details
Cooling capacity: | kW | 3.967 | 2.819 | 3.967 | 2.332 | 3.967 | 1.053 | 2.469 | 2.95 | 2.332 | 3.967
Dew point temperature: | °C | -3.3 | -3.3 | -3.3 | -3.3 | -3.3 | 2 | -1.9 | -3.3 | -3.3 | -3.3
Air inlet temperature: | °C | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 5 | 5 | 5
Mean temperature difference: | K | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8 | 11.9 | 8.3 | 8.3 | 8.3
Estimated fan power: | W | 156 | 141.8 | 184.2 | 92.58 | 156 | 39.26 | 82.86 | 400 | 210 | 210
Estimated defrost power: | W | 1136 | 1042 | 1326 | 720.8 | 1136 | 0 | 0 | 1510 | 1510 | 1510
Transmission: | kW | 1.303 | 1.363 | 1.411 | 1.241 | 1.303 | 0.535 | 1.11 | 1.059 | 0.807 | 1.539
Infiltration: | kW | 0.437 | 0.387 | 0.359 | 0.437 | 0.611 | 0.204 | 0.586 | 0.58 | 0.262 | 0.359
Ice on evaporator: | kW | 0.029 | 0.029 | 0.021 | 0.029 | 0.04 | 0 | 0 | 0.048 | 0.017 | 0.022
Goods total: | kW | 1.092 | 0.546 | 1.574 | 0 | 1.092 | 0 | 0 | 0.546 | 0.437 | 0.819
Goods, cooling: | kW | 1.092 | 0.546 | 1.574 | 0 | 1.092 | 0 | 0 | 0.546 | 0.437 | 0.819
Goods, respiration: | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Light: | kW | 0.028 | 0.028 | 0.032 | 0.028 | 0.028 | 0.028 | 0.133 | 0.037 | 0.069 | 0.014
People: | kW | 0.028 | 0.028 | 0.032 | 0.028 | 0.028 | 0.025 | 0.057 | 0.014 | 0.07 | 0.014
Fans: | kW | 0.156 | 0.142 | 0.184 | 0.093 | 0.156 | 0.039 | 0.083 | 0.4 | 0.21 | 0.21
Other: | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Defrost: | kW | 0 | 0 | 0.004 | 0.013 | 0.091 | 0.003 | 0.008 | 0.126 | 0.007 | 0.153
Total: | kW | 3.072 | 2.523 | 3.617 | 1.867 | 3.349 | 0.833 | 1.977 | 2.811 | 1.88 | 3.13
Room conditions:
Temperature: | °C | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 5 | 5 | 5
Relative humidity: |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.703 | 0.8 | 0.8 | 0.8
Operating hours: | h | 17.3 | 17.3 | 15 | 17.3 | 17.3 | 17.3 | 15 | 17.3 | 17.3 | 17.3
Inner dimensions:
Length: | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Width: | m | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Height: | m | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
Goods:
Type: |  | Mixed products | Mixed | Mixed | Mixed | Mixed | Mixed | Mixed | Mixed | Mixed | Mixed
Quantity per day: | kg | 4000 | 2000 | 5000 | 4000 | 4000 | 2000 | 4000 | 2000 | 4000 | 3000
Inlet temperature: | °C | 10 | 10 | 10 | 5 | 10 | 10 | 10 | 10 | 7 | 10
Air exchange (infiltration):
Temperature: | °C | 28 | 35 | 23 | 28 | 28 | 20 | 28 | 28 | 28 | 25
Relative humidity: |  | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.7 | 0.55 | 0.8 | 0.55 | 0.55
Door openings: |  | Regular | Rare | Regular | Regular | Often | Regular | Often | Regular | Rare | Regular
Air exchange rate: |  | 4.8 | 2.9 | 4.8 | 4.8 | 6.7 | 4.8 | 6.7 | 4.8 | 2.9 | 4.8
Heat transfer:
Panel thickness: | mm | 60 | 75 | 50 | 100 | 60 | 60 | 60 | 75 | 100 | 50
Temperature of surroundings: | °C | 28 | 35 | 23 | 28 | 28 | 20 | 28 | 28 | 28 | 28
Temperature below floor: | °C | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Floor is insulated: |  | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes
Additional loads:
Lights: | W | 240 | 240 | 240 | 240 | 240 | 240 | 500 | 640 | 240 | 240
Fans: | W | 156 | 141.8 | 184.2 | 92.58 | 156 | 39.26 | 82.86 | 400 | 210 | 210
People: | h/day | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 1 | 5 | 1
Other: | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Defrost:
Defrost type: |  | Natural | Natural | Natural | Electric | Natural | Natural | Natural | Electric | Natural | Electric
Power: | W |  |  |  | 720.8 |  |  |  | 1510 |  | 1510
Defrosts per day: |  | 4 | 4 | 4 | 2 | 4 | 4 | 3 | 4 | 4 | 4
Defrosts time: |  | 30 | 30 | 30 | 30 | 30 | 20 | 30 | 30 | 30 | 30

## transpose
Condensing Unit | Refrigerant: | Evaporating dew point temperature: | Evaporating pressure: | Useful superheat: | Additional superheat: | Return gas temperature: | Ambient temperature: | Subcooling: | Additional subcooling: | Rating conditions: | Required cooling capacity: | Model | Code number | Compressor model | Product range | Product version | Refrigerant | Cooling [kW] | COP cooling [W/W] | Total power [kW] | Total current [A] | Frequency [Hz] | Power supply | Tc [°C] | Ecodesign | Model: OP-MPXM046MLP00E. Compliant with Ecodesign 2018 | Refrigerant: R134a | Item | Evaporating temperature | Parameters at full load and ambient temperature 32,0 °C | Rated cooling capacity | Rated power input | Rated COP | Parameters at full load and ambient temperature 25,0 °C | Cooling capacity | Power input | COP | Parameters at full load and ambient temperature 43,0 °C | Cooling capacity | Power input | COP | Cold Room Controller | Power supply | Voltage | Power consumption (electronics only) | Cold room conditions | Operating temperature | Storage temperature | Relative humidity | General characteristics | Type of sensors | Resolution | Sensor read precision | Read range | Digital inputs | Requirements to contact | Output characteristics - max. applicable load (230 V AC) | Compressor | Defrost | Fans | Room light | Alarm contact (non-powered contact) | General electrical protection | Dimensions | Dimensions | Insulation / mechanical characteristics | Housing protection rating | Housing material | Type of insulation | Ordering | Code number | Liquid Line | Refrigerant: | Mass flow in line: | Evaporating temperature: | Evaporating pressure: | Useful superheat: | Additional superheat: | Discharge temperature: | Cooling capacity: | Heating capacity: | Condensing temperature: | Condensing pressure: | Subcooling: | Additional subcooling: | System and line: | Pressure drop | Saturation temperature drop | Suction Line | Refrigerant: | Mass flow in line: | Evaporating temperature: | Evaporating pressure: | Useful superheat: | Additional superheat: | Discharge temperature: | Cooling capacity: | Heating capacity: | Condensing temperature: | Condensing pressure: | Subcooling: | Additional subcooling: | System and line: | Pressure drop | Saturation temperature drop | Cold Room Details | Cooling capacity: | Dew point temperature: | Air inlet temperature: | Mean temperature difference: | Estimated fan power: | Estimated defrost power: | Transmission: | Infiltration: | Ice on evaporator: | Goods total: | Goods, cooling: | Goods, respiration: | Light: | People: | Fans: | Other: | Defrost: | Total: | Room conditions: | Temperature: | Relative humidity: | Operating hours: | Inner dimensions: | Length: | Width: | Height: | Goods: | Type: | Quantity per day: | Inlet temperature: | Air exchange (infiltration): | Temperature: | Relative humidity: | Door openings: | Air exchange rate: | Heat transfer: | Panel thickness: | Temperature of surroundings: | Temperature below floor: | Floor is insulated: | Additional loads: | Lights: | Fans: | People: | Other: | Defrost: | Defrost type: | Power: | Defrosts per day: | Defrosts time:
|  | °C | bar | K | K | °C | °C | K | K |  | kW | [16 empty] | Unit | °C |  | kW | kW |  |  | kW | kW |  |  | kW | kW | [33 empty] | kg/h | °C | bar | K | K | °C | kW | kW | °C | bar | K | K |  | bar | K |  |  | kg/h | °C | bar | K | K | °C | kW | kW | °C | bar | K | K |  | bar | K |  | kW | °C | °C | K | W | W | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW |  | °C |  | h |  | m | m | m |  |  | kg | °C |  | °C |  |  |  |  | mm | °C | °C |  |  | W | W | h/day | W |  |  | W
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 3.072 | OP-MPXM046MLP00E | 114X4284 | MLZ021T4 | Optyma™ Plus | P00 | R134a | 3.967 | 2.94 | 1.352 | 2.86 | 50 | 380 - 400 V 3 ph | 40.7 |  |  |  | Value | -10 |  | 2.998 | 1.289 | 2.33 |  | 3.217 | 1.136 | 2.83 |  | 2.634 | 1.565 | 1.68 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Liquid line | 7.755 | 44 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Suction line | 0.002 | 0 |  | 3.967 | -3.3 | 5 | 8.3 | 156 | 1136 | 1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.028 | 0.028 | 0.156 | 0 | 0 | 3.072 |  | 5 | 80% | 17.3 |  | 6 | 5 | 3.6 |  | Mixed products | 4000 | 10 |  | 28 | 55% | Regular | 4.8 |  | 60 | 28 | 10 | Yes |  | 240 | 156 | 2 | 0 |  | Natural |  | 4 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 36 | 3 | 0 | Custom | 2.523 | OP-MPXM034MLP00E | 114X4264 | MLZ015T4 | Optyma™ Plus | P00 | R134a | 2.819 | 2.57 | 1.097 | 3.014 | 50 | 380 - 400 V 3 ph | 43 |  |  |  | Value | -10 |  | 2.216 | 0.983 | 2.25 |  | 2.378 | 0.865 | 2.75 |  | 1.958 | 1.205 | 1.62 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 70.39 | -3.3 | 2.596 | 5.4 | 0 | 63.3 | 2.819 | 3.656 | 43 | 11.02 | 3 | 0 | Dry - Liquid line | 8.423 | 46.3 |  | R134a | 70.39 | -3.3 | 2.596 | 5.4 | 0 | 63.3 | 2.819 | 3.656 | 43 | 11.02 | 3 | 0 | Dry - Suction line | 0.001 | 0 |  | 2.819 | -3.3 | 5 | 8.3 | 141.8 | 1042 | 1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.028 | 0.028 | 0.142 | 0 | 0 | 2.523 |  | 5 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 2000 | 10 |  | 35 | 0.55 | Rare | 2.9 |  | 75 | 35 | 10 | Yes |  | 240 | 141.8 | 2 | 0 |  | Natural |  | 4 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 3.617 | OP-MPXM046MLP00E | 114X4284 | MLZ021T4 | Optyma™ Plus | P00 | R134a | 3.967 | 2.94 | 1.352 | 2.86 | 50 | 380 - 400 V 3 ph | 40.7 |  |  |  | Value | -10 |  | 2.998 | 1.289 | 2.33 |  | 3.217 | 1.136 | 2.83 |  | 2.634 | 1.565 | 1.68 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Liquid line | 7.755 | 44 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Suction line | 0.002 | 0 |  | 3.967 | -3.3 | 5 | 8.3 | 184.2 | 1326 | 1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 0.032 | 0.032 | 0.184 | 0 | 0.004 | 3.617 |  | 5 | 0.8 | 15 |  | 6 | 5 | 3.6 |  | Mixed | 5000 | 10 |  | 23 | 0.55 | Regular | 4.8 |  | 50 | 23 | 10 | Yes |  | 240 | 184.2 | 2 | 0 |  | Natural |  | 4 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 2.332 | OP-MPGM033AJP00G | 114X4220 | CAJ4511Y | Optyma™ Plus | P00 | R134a | 2.332 | 2.43 | 0.961 | 4.817 | 50 | 220 - 240 V 1 ph | 39.1 |  |  |  | Value | -10 |  | 1.74 | 0.849 | 2.05 |  | 1.922 | 0.811 | 2.37 |  | 1.44 | 0.897 | 1.6 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 55.94 | -3.3 | 2.596 | 5.4 | 0 | 58.5 | 2.332 | 2.949 | 39.1 | 9.913 | 3 | 0 | Dry - Liquid line | 7.318 | 42.4 |  | R134a | 55.94 | -3.3 | 2.596 | 5.4 | 0 | 58.5 | 2.332 | 2.949 | 39.1 | 9.913 | 3 | 0 | Dry - Suction line | 0.003 | 0 |  | 2.332 | -3.3 | 5 | 8.3 | 92.58 | 720.8 | 1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.028 | 0.028 | 0.093 | 0 | 0.013 | 1.867 |  | 5 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 4000 | 5 |  | 28 | 0.55 | Regular | 4.8 |  | 100 | 28 | 10 | No |  | 240 | 92.58 | 2 | 0 |  | Electric | 720.8 | 2 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 3.349 | OP-MPXM046MLP00E | 114X4284 | MLZ021T4 | Optyma™ Plus | P00 | R134a | 3.967 | 2.94 | 1.352 | 2.86 | 50 | 380 - 400 V 3 ph | 40.7 |  |  |  | Value | -10 |  | 2.998 | 1.289 | 2.33 |  | 3.217 | 1.136 | 2.83 |  | 2.634 | 1.565 | 1.68 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Liquid line | 7.755 | 44 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Suction line | 0.002 | 0 |  | 3.967 | -3.3 | 5 | 8.3 | 156 | 1136 | 1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.028 | 0.028 | 0.156 | 0 | 0.091 | 3.349 |  | 5 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 4000 | 10 |  | 28 | 0.55 | Often | 6.7 |  | 60 | 28 | 10 | Yes |  | 240 | 156 | 2 | 0 |  | Natural |  | 4 | 30
| R134a | 2 | 3.147 | 5.2 | 0 | 7.2 | 32 | 3 | 0 | Custom | 0.833 | OP-MCGC015SCA00G | 114X0448 | SC15GX | Optyma™ | A00 | R134a | 1.053 | 1.75 | 0.602 | 3.57 | 50 | 220 - 240 V 1 ph | 50.2 |  |  |  | Value | -10 |  | 0.67 | 0.463 | 1.45 |  | 0.727 | 0.446 | 1.63 |  | 0.563 | 0.492 | 1.14 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 27.8 | 2 | 3.147 | 5.2 | 0 | 69.3 | 1.053 | 1.381 | 50.2 | 13.23 | 3 | 0 | Dry - Liquid line | 10.09 | 48.2 |  | R134a | 27.8 | 2 | 3.147 | 5.2 | 0 | 69.3 | 1.053 | 1.381 | 50.2 | 13.23 | 3 | 0 | Dry - Suction line | 0.002 | 0 |  | 1.053 | 2 | 10 | 8 | 39.26 | 0 | 0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.028 | 0.025 | 0.039 | 0 | 0.003 | 0.833 |  | 10 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 2000 | 10 |  | 20 | 0.7 | Regular | 4.8 |  | 60 | 20 | 10 | Yes |  | 240 | 39.26 | 2 | 0 |  | Natural |  | 4 | 20
| R134a | -1.9 | 2.729 | 7.8 | 0 | 5.8 | 32 | 3 | 0 | Custom | 1.977 | OP-MPGM033AJP00G | 114X4220 | CAJ4511Y | Optyma™ Plus | P00 | R134a | 2.469 | 2.51 | 0.984 | 4.929 | 50 | 220 - 240 V 1 ph | 39.4 |  |  |  | Value | -10 |  | 1.74 | 0.849 | 2.05 |  | 1.922 | 0.811 | 2.37 |  | 1.44 | 0.897 | 1.6 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 58.28 | -1.9 | 2.729 | 7.8 | 0 | 60.8 | 2.469 | 3.1 | 39.4 | 10.01 | 3 | 0 | Dry - Liquid line | 7.28 | 41.4 |  | R134a | 58.28 | -1.9 | 2.729 | 7.8 | 0 | 60.8 | 2.469 | 3.1 | 39.4 | 10.01 | 3 | 0 | Dry - Suction line | 0.003 | 0 |  | 2.469 | -1.9 | 10 | 11.9 | 82.86 | 0 | 1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.133 | 0.057 | 0.083 | 0 | 0.008 | 1.977 |  | 10 | 0.703 | 15 |  | 6 | 5 | 3.6 |  | Mixed | 4000 | 10 |  | 28 | 0.55 | Often | 6.7 |  | 60 | 28 | 10 | Yes |  | 500 | 82.86 | 4 | 0 |  | Natural |  | 3 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 2.811 | OP-MPXM034MLP00E | 114X4264 | MLZ015T4 | Optyma™ Plus | P00 | R134a | 2.95 | 2.89 | 1.02 | 2.906 | 50 | 380 - 400 V 3 ph | 39.1 |  |  |  | Value | -10 |  | 2.216 | 0.983 | 2.25 |  | 2.378 | 0.865 | 2.75 |  | 1.958 | 1.205 | 1.62 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 70.8 | -3.3 | 2.596 | 5.4 | 0 | 58.6 | 2.95 | 3.731 | 39.1 | 9.933 | 3 | 0 | Dry - Liquid line | 7.337 | 42.4 |  | R134a | 70.8 | -3.3 | 2.596 | 5.4 | 0 | 58.6 | 2.95 | 3.731 | 39.1 | 9.933 | 3 | 0 | Dry - Suction line | 0.001 | 0 |  | 2.95 | -3.3 | 5 | 8.3 | 400 | 1510 | 1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 0.037 | 0.014 | 0.4 | 0 | 0.126 | 2.811 |  | 5 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 2000 | 10 |  | 28 | 0.8 | Regular | 4.8 |  | 75 | 28 | 10 | Yes |  | 640 | 400 | 1 | 0 |  | Electric | 1510 | 4 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 1.88 | OP-MPGM033AJP00G | 114X4220 | CAJ4511Y | Optyma™ Plus | P00 | R134a | 2.332 | 2.43 | 0.961 | 4.817 | 50 | 220 - 240 V 1 ph | 39.1 |  |  |  | Value | -10 |  | 1.74 | 0.849 | 2.05 |  | 1.922 | 0.811 | 2.37 |  | 1.44 | 0.897 | 1.6 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 55.94 | -3.3 | 2.596 | 5.4 | 0 | 58.5 | 2.332 | 2.949 | 39.1 | 9.913 | 3 | 0 | Dry - Liquid line | 7.318 | 42.4 |  | R134a | 55.94 | -3.3 | 2.596 | 5.4 | 0 | 58.5 | 2.332 | 2.949 | 39.1 | 9.913 | 3 | 0 | Dry - Suction line | 0.003 | 0 |  | 2.332 | -3.3 | 5 | 8.3 | 210 | 1510 | 0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.069 | 0.07 | 0.21 | 0 | 0.007 | 1.88 |  | 5 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 4000 | 7 |  | 28 | 0.55 | Rare | 2.9 |  | 100 | 28 | 10 | Yes |  | 240 | 210 | 5 | 0 |  | Natural |  | 4 | 30
| R134a | -3.3 | 2.596 | 5.4 | 0 | 2.1 | 32 | 3 | 0 | Custom | 3.13 | OP-MPXM046MLP00E | 114X4284 | MLZ021T4 | Optyma™ Plus | P00 | R134a | 3.967 | 2.94 | 1.352 | 2.86 | 50 | 380 - 400 V 3 ph | 40.7 |  |  |  | Value | -10 |  | 2.998 | 1.289 | 2.33 |  | 3.217 | 1.136 | 2.83 |  | 2.634 | 1.565 | 1.68 |  |  | 230 V~ ± 10% 50Hz / 60Hz | ~ 7 VA |  | -5 to 50°C | -10 to 70°C | Less than 90% - Not condensed. No shock influence/vibration. |  | EKS 221, code no.: 084N3210 | 0.1 K | ± 0.5 K | -45…+45 °C |  | Gold plating |  | 1500W (AC3) | 3000W (AC1) | 500W (AC3) | 800W (AC1) | 100W | Automatic fuse 16A. Id=300 mA. Disconnecting power 4.5 kA |  | 168 mm x 97 mm x 262 mm (HxPxL) |  | IP65 | Self-extinguishing ABS | Class II |  | 080Z3200 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Liquid line | 7.755 | 44 |  | R134a | 96.69 | -3.3 | 2.596 | 5.4 | 0 | 60.5 | 3.967 | 5.068 | 40.7 | 10.35 | 3 | 0 | Dry - Suction line | 0.002 | 0 |  | 3.967 | -3.3 | 5 | 8.3 | 210 | 1510 | 1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.014 | 0.014 | 0.21 | 0 | 0.153 | 3.13 |  | 5 | 0.8 | 17.3 |  | 6 | 5 | 3.6 |  | Mixed | 3000 | 10 |  | 25 | 0.55 | Regular | 4.8 |  | 50 | 28 | 10 | Yes |  | 240 | 210 | 1 | 0 |  | Electric | 1510 | 4 | 30

## test
Transmission: | Infiltration: | Ice on evaporator: | Goods total: | Goods, cooling: | Goods, respiration: | Light: | People: | Fans: | Other: | Defrost: | Measure
1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.083 | 0 | 0.008 | people to often in room
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.028 | 1 | 0.142 | 3 | 0 | Too many people
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 1 | 0.014 | 0.4 | 0 | 0.126 | Change the lighting
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.069 | 0.07 | 0.21 | 0 | 0.007 | nothing

## train
Transmission: | Infiltration: | Ice on evaporator: | Goods total: | Goods, cooling: | Goods, respiration: | Light: | People: | Fans: | Other: | Defrost: | Measure
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.028 | 0.028 | 0.156 | 0 | 0 | nothing
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.028 | 0.028 | 0.142 | 0 | 0 | nothing
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 0.032 | 0.032 | 0.184 | 0 | 0.004 | nothing
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.028 | 0.028 | 0.093 | 0 | 0.013 | nothing
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.028 | 0.028 | 0.156 | 0 | 0.091 | nothing
0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.028 | 0.025 | 0.039 | 0 | 0.003 | nothing
1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.133 | 0.057 | 0.083 | 0 | 0.008 | nothing
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 0.037 | 0.014 | 0.4 | 0 | 0.126 | nothing
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.069 | 0.07 | 0.21 | 0 | 0.007 | nothing
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.014 | 0.014 | 0.21 | 0 | 0.153 | nothing
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.028 | 0.028 | 0.156 | 0 | 0 | nothing
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.028 | 0.028 | 0.142 | 0 | 0 | nothing
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 0.032 | 0.032 | 0.184 | 0 | 0.004 | nothing
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.028 | 0.028 | 0.093 | 0 | 0.013 | nothing
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.028 | 0.028 | 0.156 | 0 | 0.091 | nothing
0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.028 | 0.025 | 0.039 | 0 | 0.003 | nothing
1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.133 | 0.057 | 0.083 | 0 | 0.008 | nothing
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 0.037 | 0.014 | 0.4 | 0 | 0.126 | nothing
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.069 | 0.07 | 0.21 | 0 | 0.007 | nothing
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.014 | 0.014 | 0.21 | 0 | 0.153 | nothing
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.028 | 1 | 0.156 | 0 | 0 | Too many people
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 3.028 | 1 | 0.142 | 0 | 0 | Too many people
1.411 | 0.359 | 0.421 | 1.574 | 1.574 | 0 | 0.032 | 1 | 0.184 | 0 | 0.004 | Too many people
3.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.028 | 1 | 0.093 | 0 | 0.013 | Too many people
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.028 | 1 | 0.156 | 0 | 0.091 | Too many people
0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.028 | 1 | 0.039 | 0 | 0.003 | Too many people
1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.133 | 1 | 0.083 | 0 | 0.008 | Too many people
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 0.037 | 1 | 0.4 | 0 | 0.126 | Too many people
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.069 | 1 | 0.21 | 0 | 0.007 | Too many people
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.014 | 1 | 0.21 | 0 | 0.153 | Too many people
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.028 | 1 | 0.156 | 0 | 0 | Too many people
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.028 | 1 | 0.142 | 3 | 0 | Too many people
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 0.032 | 1 | 0.184 | 0 | 0.24 | Too many people
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.028 | 1 | 0.093 | 0 | 0.013 | Too many people
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.028 | 1 | 0.156 | 0 | 0.091 | Too many people
0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.028 | 1 | 0.039 | 0 | 0.003 | Too many people
2.11 | 0.586 | 0 | 0 | 0 | 0 | 0.133 | 1 | 0.083 | 0 | 0.008 | Too many people
1.059 | 0.58 | 0.248 | 0.546 | 0.546 | 0 | 0.037 | 1 | 0.4 | 0 | 0.126 | Too many people
0.807 | 0.262 | 0.017 | 1.437 | 0.437 | 0 | 0.069 | 1 | 0.21 | 0 | 0.007 | Too many people
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.414 | 1 | 0.21 | 0 | 0.153 | Too many people
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 1 | 0.028 | 0.156 | 0 | 0 | Change the lighting
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 1 | 0.028 | 0.142 | 0 | 0 | Change the lighting
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 1 | 0.032 | 0.184 | 0 | 0.004 | Change the lighting
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 1 | 0.028 | 0.093 | 0 | 0.013 | Change the lighting
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 1 | 0.028 | 0.156 | 0 | 0.091 | Change the lighting
0.535 | 0.204 | 0 | 0 | 0 | 0 | 1 | 0.025 | 0.039 | 0 | 0.003 | Change the lighting
1.11 | 0.586 | 0 | 0 | 0 | 0 | 1 | 0.057 | 0.083 | 0 | 0.008 | Change the lighting
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 1 | 0.014 | 0.4 | 0 | 0.126 | Change the lighting
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 1 | 0.07 | 0.21 | 0 | 0.007 | Change the lighting
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 1 | 0.014 | 0.21 | 0 | 0.153 | Change the lighting
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 1 | 0.028 | 0.156 | 0 | 0 | Change the lighting
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 1 | 0.028 | 0.142 | 0 | 0 | Change the lighting
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 1 | 0.032 | 0.184 | 0 | 0.004 | Change the lighting
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 1 | 0.028 | 0.093 | 0 | 0.013 | Change the lighting
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 1 | 0.028 | 0.156 | 0 | 0.091 | Change the lighting
0.535 | 0.204 | 0 | 0 | 0 | 0 | 1 | 0.025 | 0.039 | 0 | 0.003 | Change the lighting
1.11 | 0.586 | 0 | 0 | 0 | 0 | 1 | 0.057 | 0.083 | 0 | 0.008 | Change the lighting
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 1 | 0.014 | 0.4 | 0 | 0.126 | Change the lighting
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 1 | 0.07 | 0.21 | 0 | 0.007 | Change the lighting
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 1 | 0.014 | 0.21 | 0 | 0.153 | Change the lighting
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.5 | 0.5 | 0.156 | 0 | 0 | people to often in room
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.5 | 0.5 | 0.142 | 0 | 0 | people to often in room
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 0.5 | 0.5 | 0.184 | 0 | 0.004 | people to often in room
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.5 | 0.5 | 0.093 | 0 | 0.013 | people to often in room
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.5 | 0.5 | 0.156 | 0 | 0.091 | people to often in room
0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.039 | 0 | 0.003 | people to often in room
1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.083 | 0 | 0.008 | people to often in room
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 0.5 | 0.5 | 0.4 | 0 | 0.126 | people to often in room
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.5 | 0.5 | 0.21 | 0 | 0.007 | people to often in room
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.5 | 0.5 | 0.21 | 0 | 0.153 | people to often in room
1.303 | 0.437 | 0.029 | 1.092 | 1.092 | 0 | 0.5 | 0.5 | 0.156 | 0 | 0 | people to often in room
1.363 | 0.387 | 0.029 | 0.546 | 0.546 | 0 | 0.5 | 0.5 | 0.142 | 0 | 0 | people to often in room
1.411 | 0.359 | 0.021 | 1.574 | 1.574 | 0 | 0.5 | 0.5 | 0.184 | 0 | 0.004 | people to often in room
1.241 | 0.437 | 0.029 | 0 | 0 | 0 | 0.5 | 0.5 | 0.093 | 0 | 0.013 | people to often in room
1.303 | 0.611 | 0.04 | 1.092 | 1.092 | 0 | 0.5 | 0.5 | 0.156 | 0 | 0.091 | people to often in room
0.535 | 0.204 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.039 | 0 | 0.003 | people to often in room
1.11 | 0.586 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.083 | 0 | 0.008 | people to often in room
1.059 | 0.58 | 0.048 | 0.546 | 0.546 | 0 | 0.5 | 0.5 | 0.4 | 0 | 0.126 | people to often in room
0.807 | 0.262 | 0.017 | 0.437 | 0.437 | 0 | 0.5 | 0.5 | 0.21 | 0 | 0.007 | people to often in room
1.539 | 0.359 | 0.022 | 0.819 | 0.819 | 0 | 0.5 | 0.5 | 0.21 | 0 | 0.153 | people to often in room